Raspberry Pi MQTT Broker

Configuration & Build Record

Rev 0.3  •  April 3, 2026  •  Status: Operational — Wired Ethernet / Static IP Pending

1.  Overview

This document records the configuration, build history, and operational status of a dedicated Mosquitto MQTT broker running on a Raspberry Pi 4B. The broker serves as the central UNS message bus for the Loogootee Manufacturing training rack — receiving Sparkplug B publications from edge devices and making data available to subscribers including Node-RED and SCADA clients.

2.  Hardware

| Device | Raspberry Pi 4B — 4GB RAM |
| --- | --- |
| Enclosure | Phoenix Contact RPI-BC DIN Rail Housing (DIN 43880) |
| Power | PoE — Cisco SG300-28PP-K9 (802.3at PoE+) |
| PoE Hat | Temporary — original hat included with used Pi. Replacement: PoE Texas RPi PoE+ Hat with integrated fan and opto-isolation (arriving Saturday) |
| Storage | Samsung T7 500GB USB-C SSD (cloned from 64GB flash drive, April 3 2026) |
| Network | WiFi — temporary. Wired ethernet to Cisco switch pending PoE+ hat swap |
| Cooling | No active cooling currently. Integrated fan on replacement PoE+ hat will address this |

Thermal note: Idle temp observed at 45–50°C on current hardware without active cooling. Reading of 59.4°C on April 3 attributed to proximity to laptop exhaust — not representative of true idle baseline. Target idle temp with integrated fan expected mid-30s°C.

3.  Operating System & Software

| OS | Raspberry Pi OS Lite 64-bit (Debian-based) |
| --- | --- |
| Kernel | 6.12.75+rpt-rpi-v8 |
| Hostname | RasPiMosquitoBroker |
| Mosquitto Version | 2.0.21 |
| Broker Service | Active and enabled (starts on boot) |
| Listener Ports | 1883 — IPv4 and IPv6 |
| Firewall | ufw — enabled |
| Brute-Force Protection | fail2ban — installed and active |

4.  Boot Configuration

The Pi boots from the Samsung T7 SSD via USB. The bootloader EEPROM was repaired and reconfigured during initial setup. Boot order and startup delay were modified to ensure reliable USB boot detection.

Bootloader EEPROM Config

BOOT_ORDER=0xf41

USB_MSD_STARTUP_DELAY=20000

Boot order 0xf41: USB mass storage first, SD card second, repeat. Startup delay of 20,000ms (20 seconds) allows time for USB drive initialization before bootloader gives up.

Boot Issue Resolved — April 3, 2026

Initial boot from Samsung T7 failed due to PARTUUID mismatch between the boot partition cmdline.txt and the actual root partition. Root cause: clone was performed while Samsung was assigned device sdb; after reboot as boot device it became sda, resulting in a different PARTUUID being assigned.

Fix applied: mounted Samsung boot partition, corrected cmdline.txt PARTUUID to match actual root partition:

root=PARTUUID=41867edd-02

5.  Mosquitto Configuration

Configuration File Location

/etc/mosquitto/conf.d/broker.conf

Configuration Contents

allow_anonymous false

password_file /etc/mosquitto/passwd

listener 1883

persistence true

persistence_location /var/lib/mosquitto/

log_dest syslog

log_dest stdout

6.  Authentication

| Authentication | Enabled — anonymous access disabled |
| --- | --- |
| Password File | /etc/mosquitto/passwd |
| Permissions | Owned by mosquitto:mosquitto, chmod 600 |
| Current Users | broker (initial test credential — password updated from default) |
| Planned Users | Separate credentials per client class: EPIC publisher, Node-RED subscriber, additional controllers as integrated |

⚠  Credentials per client class to be configured prior to first rack device connection.

7.  Firewall & Security

| Firewall | ufw — active |
| --- | --- |
| Allowed: SSH | 22/tcp — IPv4 and IPv6 |
| Allowed: MQTT | 1883/tcp — IPv4 and IPv6 |
| All other ports | Denied |
| fail2ban | Installed — SSH brute-force protection active |

8.  Network

| Current Connection | WiFi — temporary |
| --- | --- |
| Current IP | 10.0.4.43 (DHCP assigned — subject to change) |
| Target Connection | Wired ethernet — Cisco SG300-28PP-K9 |
| Target IP | Static DHCP reservation via Cisco switch — pending |
| SSH Access | ssh broker@RasPiMosquitoBroker.local or ssh broker@[IP address] |

⚠  Static IP reservation to be configured on Cisco switch after PoE+ hat swap and wired ethernet connection confirmed.

⚠  WiFi to be disabled via rfkill after wired connection verified.

9.  Operational Reference

SSH Access

ssh broker@RasPiMosquitoBroker.local

ssh broker@[IP address]

Health Checks

vcgencmd get_throttled

vcgencmd measure_temp

sudo systemctl status mosquitto

sudo ufw status

Broker Control

sudo systemctl restart mosquitto

sudo systemctl stop mosquitto

sudo systemctl start mosquitto

Test Publish / Subscribe

mosquitto_sub -h localhost -u broker -P [password] -t test/topic

mosquitto_pub -h localhost -u broker -P [password] -t test/topic -m "hello"

Add MQTT User

sudo mosquitto_passwd /etc/mosquitto/passwd [username]

10.  Pending Items — Rev 0.4

- Swap to PoE Texas PoE+ Hat with integrated fan (Saturday)

- Connect wired ethernet to Cisco SG300-28PP-K9

- Verify SSH access over wired connection

- Assign static DHCP reservation on Cisco switch

- Disable WiFi: sudo rfkill block wifi

- Configure per-client MQTT credentials (EPIC, Node-RED, controllers)

- Document final static IP in Section 8

- Record baseline idle temperature with fan installed

- Update to Rev 0.4 on completion

Loogootee Manufacturing Training Rack  •  RasPiMosquitoBroker  •  Rev 0.3  •  April 3, 2026